## Slide 1
Nutrient Removal
Introduction and Overview
University of Kansas
100th Annual Water and Wastewater School
Lawrence, Kansas
July 30, 2019
Grant Weaver, PE & wastewater operator
G.Weaver@CleanWaterOps.com

## Slide 2: Operational Strategies for Nutrient Removal
Nutrient Removal Overview
Nitrogen Removal
Science & Technology
Applying what we’ve learned
Phosphorus Removal
Science & Technology
Applying what we’ve learned
Aero-Mod Phosphorus and Nitrogen Removal

## Slide 3: Nutrient Removal Overview
What are Nutrients?
  Nitrogen
  Phosphorus

## Slide 4: Nutrient Removal Overview
What are Nutrients?
  Nitrogen (total-Nitrogen, including organic-Nitrogen, Ammonia, Nitrite and Nitrate)
  Phosphorus

## Slide 5: Nutrient Removal Overview
What are Nutrients?
  Nitrogen (total-Nitrogen, including organic-Nitrogen, Ammonia, Nitrite and Nitrate)
  Phosphorus (total-Phosphorus including orthophosphate, ortho-P, and insoluble P)

## Slide 6: Nutrient Removal Overview
What are Nutrients?
  Nitrogen (total-Nitrogen, including organic-Nitrogen, Ammonia, Nitrite and Nitrate)
  Phosphorus (total-Phosphorus including orthophosphate, ortho-P, and insoluble P)
Why Should Operators Care About Nutrient Removal?
  Algae blooms, Eutrophication
  Because EPA and states are putting N&P limits in municipal permits

## Slide 7: Nutrient Removal Overview
What are Nutrients?
  Nitrogen (total-Nitrogen, including organic-Nitrogen, Ammonia, Nitrite and Nitrate)
  Phosphorus (total-Phosphorus including orthophosphate, ortho-P, and insoluble P)
Why Should Operators Care About Nutrient Removal?
  Algae blooms, Eutrophication
  Because EPA and states are putting N&P limits in municipal permits
How to Remove?
  Nitrogen: Biologically
  Phosphorus: Chemically, Biologically, or Combination

## Slide 8: Nutrient Removal Overview
What are Nutrients?
  Nitrogen (total-Nitrogen, including organic-Nitrogen, Ammonia, Nitrite and Nitrate)
  Phosphorus (total-Phosphorus including orthophosphate, ortho-P, and insoluble P)
Why Should Operators Care About Nutrient Removal?
  Algae blooms, Eutrophication
  Because EPA and states are putting N&P limits in municipal permits
How to Remove?
  Nitrogen: Biologically
  Phosphorus: Chemically, Biologically, or Combination
  At What Cost?
  Facility Upgrades: generally very expensive
  Optimization: often almost free

## Slide 9: Kansas Nutrient Reduction Strategy
Conceived in 2004 as an alternative to establishing numeric nutrient criteria
Major Mechanical Plants were asked to assess feasibility and cost of nutrient removal at three levels:
Biological Nutrient Removal: TP – 1.5 mg/l; TN – 8 mg/l
[later evolved to 1 mg/l TP & 10 mg/l TN]
Enhanced Nutrient Removal: TP – 0.5 mg/l; TN – 5 mg/l
Limits of Technology: TP – 0.3 mg/l; TN – 3 mg/l
Priority of Total Maximum Daily Loads over 2012 – 2022 emphasized phosphorus & nitrate impairments
Wasteload Allocations (WLAs) from TMDLs based on BNR or ENR goals and design flows
Wasteload Allocations for Lagoons assumed they could achieve 2 mg/l TP & 10 mg/l TN
Permit Limits are mass-based (pounds/day) from WLAs required as rolling 12-month averages
TN limits established as Ammonia (2013 acute & chronic criteria) & Nitrate limit of 10 mg/l,
if required by a Nitrate TMDL
Antidegradation Review of New or Expanding Mechanical Plants typically impose ENR based limits

## Slide 10: Kansas Nutrient Reduction Strategy
total-Nitrogen total-Phosphorus
Mechanical Plants 10 mg/L 1.0 mg/L
Lagoons no change no change

## Slide 11
Historical approach: Technology!

## Slide 12: Cost of Nutrient Removal: Construction Costs and Operation & Maintenance Costs for a … 1 MGD wastewater treatment plant
Kansas Average
Design & Construct
10 mg/L Nitrogen Removal
and 1 mg/L Phosphorus Removal: $8 million

## Slide 13
SBR:
Sequencing Batch Reactor

## Slide 14
Oxidation Ditch with pre-anaerobic zone

## Slide 15
MLE:
Modified Luczak-Ettinger

## Slide 16
Modified Johannesburg

## Slide 17
New way of thinking:
Operators’ skills matter!

## Slide 18
Change day-to-day operations to
create ideal habitats for bacteria to remove Nitrogen & Phosphorus

## Slide 19
Montana
Bigfork
Big Sky
Billings
Boulder
Bozeman
Butte
Chinook
Choteau
Colstrip
Columbia Falls
Conrad
Dillon
East Helena
Forsyth
Glendive
Great Falls
Hamilton
Hardin
Havre
Helena
Kalispell
Laurel
Lewistown
Libby
Lolo
Miles City
Missoula
New Hampshire
Keene
South Carolina
Greeneville
Tennessee
Athens
Baileyton
Bartlett
Collierville
Cookeville
Crossville
Humboldt
Lafayette
LaFollette
Livingston
Millington
Missoula
Nashville
Norris
Oak Ridge
Connecticut
Colchester-East Hampton
East Haddam
Farmington
Groton
New Canaan
New Hartford
Plainfield
Portland
Suffield
Windham
Iowa
Eldora
Kansas
Basehor
Eudora
Hiawatha
Holden
Lansing
Osawatomie
Shawnee Co. Sherwood
Spring Hill
St. Marys
Topeka North
Wellsville
Texas
Nottingham MUD (Houston)
Virginia
Strasburg
Wyoming
Laramie
Kentucky
Hopkinsville
Massachusetts
Amherst
Barnstable
Easthampton
Greenfield
Montague
Newburyport
Northfield
Palmer
South Deerfield
South Hadley
Sunderland
Upton
Westfield

## Slide 21
Notes: [Grant picks it up here]
The average unit costs for the upgraded facilities were 521 times greater than the average unit costs for the optimized conventional plants.
Capital Improvement:
It’s what we do … make changes that are “guaranteed” to remove nutrients for next 20 years.
Optimization:
Practical, get-the-most with what you have first step to fixing environmental issues.
Sometimes the first and last step!
Optimization is a good approach to try first to meet new or anticipated nutrient reduction goals because:
It’s low-cost
It can reach achieve relatively low effluent levels
It is applicable to a wide-variety of plant types, influent characteristics, and climatic conditions

## Slide 22
Notes: [Grant picks it up here]
The average unit costs for the upgraded facilities were 521 times greater than the average unit costs for the optimized conventional plants.
Capital Improvement:
It’s what we do … make changes that are “guaranteed” to remove nutrients for next 20 years.
Optimization:
Practical, get-the-most with what you have first step to fixing environmental issues.
Sometimes the first and last step!
Optimization is a good approach to try first to meet new or anticipated nutrient reduction goals because:
It’s low-cost
It can reach achieve relatively low effluent levels
It is applicable to a wide-variety of plant types, influent characteristics, and climatic conditions

## Slide 23
Comparing Performance of Montana's BNR Facilities and |  |  |  |  |  |  |  |  |  | 
Optimized Conventional Wastewater Treatment Plants |  |  |  |  |  |  |  |  |  | 
Advanced (BNR) WWTFs |  |  |  |  |  | Conventional WWTFs |  |  |  | 
 | total-N |  | total-P |  |  |  | total-N |  | total-P | 
Bozeman, MT | 5 | mg/L | 0.3 | mg/L |  | Chinook, MT | 3 | mg/L | 1.2 | mg/L
Missoula, MT | 9 | mg/L | 0.2 | mg/L |  | Conrad, MT | 7 | mg/L | 0.1 | mg/L
Kalispell, MT | 8 | mg/L | 0.2 | mg/L |  | Hardin, MT | 5 | mg/L | 2.4 | mg/L
Lewistown, MT | 2 | mg/L | 1.0 | mg/L |  | Hamilton, MT | 3 | mg/L | 4.0 | mg/L
Combined Cost: $70 million |  |  |  |  |  | Combined Cost: $20,000 |  |  |  | 
Notes: [Grant picks it up here]
The average unit costs for the upgraded facilities were 521 times greater than the average unit costs for the optimized conventional plants.
Capital Improvement:
It’s what we do … make changes that are “guaranteed” to remove nutrients for next 20 years.
Optimization:
Practical, get-the-most with what you have first step to fixing environmental issues.
Sometimes the first and last step!
Optimization is a good approach to try first to meet new or anticipated nutrient reduction goals because:
It’s low-cost
It can reach achieve relatively low effluent levels
It is applicable to a wide-variety of plant types, influent characteristics, and climatic conditions

## Slide 24
Nitrogen Removal without Facility Upgrades
t-N Before t-N After
Suffield, CT 7 2
Chinook, MT 26 3
Hardin, MT 18 4
Conrad, MT 35 5
Montague, MA 30 5
Cookeville, TN 25 5
Upton, MA 22 6
Plainfield, CT 25 10
Colchester-East Hampton, CT 24 12
Big Sky, MT 25 14
Libby, MT 32 21

## Slide 25
Phosphorus Removal without Facility Upgrades
t-P Before t-P After
Conrad, MT 2.1 0.2
Chinook, MT 2.8 0.3
Westfield, MA 1.0 0.5*
Palmer, MA 0.65 0.65*
Cookeville, TN 3 0.8
Montague, MA 3 0.9
Athens, TN 3 1.8*
*chemical reduction of 50% or more

## Slide 27: Wastewater treatment for Beginning Operators
Grow bacteria that feed on soluble pollutants
Settle out the bacteria
Send clean water into the stream

## Slide 28: Wastewater treatment for Advanced Operators
Grow bacteria that feed on soluble pollutants by maintaining optimal living conditions for the bacteria that treat wastewater
    BOD
    Nitrogen
    Phosphorus
    Alkalinity / pH

## Slide 29: Wastewater treatment for Advanced Operators
Grow bacteria that feed on soluble pollutants by maintaining optimal living conditions for the bacteria that treat wastewater
    BOD
    Nitrogen
    Phosphorus
    Alkalinity / pH
Settle out the bacteria by managing clarifiers and excellent process control

## Slide 30: Wastewater treatment for Advanced Operators
Grow bacteria that feed on soluble pollutants by maintaining optimal living conditions for the bacteria that treat wastewater
    BOD
    Nitrogen
    Phosphorus
    Alkalinity / pH
Settle out the bacteria by managing clarifiers and excellent process control
Send cleaner water into the stream

## Slide 31: Wastewater treatment for Advanced Operators
Grow bacteria that feed on soluble pollutants by maintaining optimal living conditions for the bacteria that treat wastewater
    BOD
    Nitrogen
    Phosphorus
    Alkalinity / pH
Settle out the bacteria by managing clarifiers and excellent process control
Send cleaner water into the stream
Create the right conditions to maximize the controlled release of nitrogen gas

## Slide 32
Step 1: Convert Ammonia (NH4) to Nitrate (NO3)
Step 2: Convert Nitrate (NO3) to Nitrogen Gas (N2)
          Oxygen-rich
          BOD-poor
          pH of 6.5 or more
          Oxygen-poor
          BOD-rich

## Slide 33
Step 1. Prepare “dinner”
  BOD-rich
  Zero oxygen: anaerobic / fermentation
Step 2. Take bio-P bugs to “dinner”
Step 3. Grow bio-P bugs
  Move food to bio-P bugs (PAOs) – or – move bio-P bugs to food
  Zero oxygen: anaerobic / fermentation
  Same tank
  or, not
  Oxygen-rich
  pH of at least 6.8

## Slide 35
Cookeville, Tennessee Population: 33,500 15 MGD design flow

## Slide 40
Palmer, Massachusetts Population: 12,200 5.6 MGD design

## Slide 45
Conrad, Montana Population: 2,500 0.5 MGD design flow

## Slide 50
Chinook, Montana Population: 1,250 0.5 MGD design flow

## Slide 55
Helena, Montana Population: 31,500 5.4 MGD design flow

## Slide 60: Comments & Questions
Grant Weaver
g.weaver@cleanwaterops.com