## Slide 1
Nitrogen Removal
University of Kansas
100th Annual Water and Wastewater School
Lawrence, Kansas
July 30, 2019
Grant Weaver, PE & wastewater operator
G.Weaver@CleanWaterOps.com

## Slide 2: Operational Strategies for Nutrient Removal
Nutrient Removal Overview
Nitrogen Removal
Science & Technology
Applying what we’ve learned
Phosphorus Removal
Science & Technology
Applying what we’ve learned
Aero-Mod Phosphorus and Nitrogen Removal

## Slide 4
Wastewater Science
Alkalinity and pH

## Slide 5
Wastewater Science
DO and ORP
DO (Dissolved Oxygen)
ORP (Oxygen Reduction Potential)

## Slide 8
Biological Nitrogen Removal:
Convert LIQUID to GAS …
BOD and TSS Removal:
Convert LIQUID to SOLID …

## Slide 9
Step 1: Convert Ammonia (NH4) to Nitrate (NO3)
Step 2: Convert Nitrate (NO3) to Nitrogen Gas (N2)
          Oxygen-rich Aerobic Process
          Don’t need BOD for bacteria to grow
          Bacteria are sensitive to pH and temperature
          Oxygen-poor Anoxic Process
          Do need BOD for bacteria to grow
          Bacteria are hardy

## Slide 10
Ammonia (NH4)
Ammonia Removal
Ammonia (NH4) is converted to Nitrate (NO3)

## Slide 11: Ammonia Removal
Ammonia (NH4)
Oxygen (O2)

## Slide 12: Ammonia Removal
Ammonia (NH4)
Alkalinity
Oxygen (O2)
H+

## Slide 13: Ammonia Removal
Ammonia (NH4)
Nitrite (NO2)
Alkalinity
Oxygen (O2)
H+

## Slide 14: Ammonia Removal
Ammonia (NH4)
Nitrite (NO2)
Alkalinity
Oxygen (O2)
Oxygen (O2)
H+

## Slide 15: Ammonia Removal
Ammonia (NH4)
Nitrite (NO2)
Nitrate (NO3)
Alkalinity
Oxygen (O2)
Oxygen (O2)
        Nitrification Habitat:
          High DO / +ORP
          Low BOD
          High MLSS/MCRT
          High HRT
          Consumes oxygen
          Consumes alkalinity: lowers pH
H+

## Slide 16
Nitrification:
Ammonia (NH4) is converted to Nitrate (NO3)
  Oxygen Rich Habitat
          MLSS* of 2500+ mg/L (High Sludge Age / MCRT / low F:M)
          ORP* of +100 to +150 mV (High DO)
          Time* (high HRT … 24 hr, 12 hr, 6 hr)
          Low BOD
          Consumes Oxygen
          Adds acid - Consumes 7 mg/L alkalinity per mg/L of NH4 → NO3
  *Approximate, each facility is different.

## Slide 17
Biological Nitrogen Removal:
Next step:
the Nitrate (NO3) created during Nitrification …
is converted to Nitrogen Gas (N2)

## Slide 18: Nitrate Removal
Nitrate (NO3)

## Slide 19: Nitrate Removal
Nitrate (NO3)
BOD

## Slide 20: Nitrate Removal
Nitrate (NO3)
Nitrogen Gas (N2)
BOD

## Slide 21: Nitrate Removal
Nitrate (NO3)
Nitrogen Gas (N2)
Oxygen
BOD

## Slide 22: Nitrate Removal
Nitrate (NO3)
Nitrogen Gas (N2)
Alkalinity
Oxygen
BOD
Denitrification Habitat:
  Low DO / -ORP
  High BOD
  Adds DO
  Gives back ½ the alkalinity: beneficially raises pH

## Slide 23
Denitrification:
Nitrate (NO3) is converted to Nitrogen Gas (N2)
  Oxygen Poor Habitat
          ORP* of -100 mV or less (DO < 0.3 mg/L)
          Surplus BOD* (100-250 mg/L: 5-10 times as much as NO3)
          Retention Time* of 45-90 minutes
          Gives back Oxygen
          Gives back Alkalinity (3.5 mg/L per mg/L of NO3 → N2)
    *Approximate, each facility is different.

## Slide 24
Nitrogen Removal
 | 1. Nitrification | 2. Denitrification
 | Ammonia Removal | Nitrate Removal
 | NH4→NO3 | NO3→N2
DO: Dissolved Oxygen | >1 mg/L | <0.3 mg/L
ORP: Oxygen Reduction Potential | >+100 mV | <-100 mV
MLSS | >2500 mg/L | >2500 mg/L
HRT (Hydraulic Retention Time) | >6 hr | ~1 hr
BOD: Biochemical Oxygen Demand | <20 mg/L | >100 mg/L
Alkalinity | >60 mg/L | NA
 | Alkalinity is lost | Alkalinity is gained
Notes: |  | 
> means "greater than" |  | 
< means "less than" |  | 
~ means "approximately“ All numbers are “rules of thumb” |  | 

## Slide 25
Technology!

## Slide 26
Post Denitrification

## Slide 27
BOD
Secondary
Clarifier
Post-Anoxic Denitrification
Anoxic Zone
Aerobic Zone
NH4
NO3
NO3
N2
          Ammonia (NH4) Removal
          Target: NH4 < 0.5 mg/L
          Nitrate (NO3) Removal
          Target NO3 in Anoxic Tank: 0.5-2 mg/L

## Slide 28
MLE Process
(Modified Ludzack-Ettinger)

## Slide 29
Internal Recycle
Secondary
Clarifier
Return Sludge
Aerobic Zone
Anoxic Zone
NH4
NO3
MLE (Modified Ludzack-Ettinger) Process

## Slide 30
Internal Recycle
Secondary
Clarifier
Return Sludge
Aerobic Zone
Anoxic Zone
NH4
MLE (Modified Ludzack-Ettinger) Process
NO3

## Slide 31
Internal Recycle
Secondary
Clarifier
Return Sludge
Aerobic Zone
Anoxic Zone
NH4
N2
MLE (Modified Ludzack-Ettinger) Process
          Ammonia (NH4) Removal
          Target: NH4: 0.5 mg/L
          Nitrate (NO3) Removal
          Target NO3 in Anoxic Tank: 2 mg/L
NO3

## Slide 32
Internal Recycle
Secondary
Clarifier
Return Sludge
Aerobic Zone
Anoxic Zone
MLE (Modified Ludzack-Ettinger) Process
NH4
NO3
N2
NO3
MLE Process Control:
Proper Internal Recycle Rate; not too much / not too little.
ORP of +100 mV in Aerobic Zone for Ammonia (NH4) Removal.
ORP of -75 to -150 mV in Anoxic Zone for Nitrate (NO3) Removal.
Enough BOD to support Nitrate (NO3) Removal.

## Slide 33
Internal Recycle
Secondary
Clarifier
Return Sludge
Aerobic Zone
Anoxic Zone
NH4
N2
NO3
NO3
          Nitrate (NO3) Removal
          Great Anoxic Habitat: ORP -150 mV or lower
          NO3 > 4 mg/L because too little NO3 is returned to Anoxic Zone
          Ammonia (NH4) Removal
          Excellent Aerobic Habitat: ORP +150 mV
          NH4 < 0.5 mg/L
MLE with not enough Internal Recycle

## Slide 34
Internal Recycle
Secondary
Clarifier
Return Sludge
Aerobic Zone
Anoxic Zone
NH4
N2
NO3
NO3
          Nitrate (NO3) Removal
          Stressed Anoxic Habitat: ORP 0 to -100 mV
          NO3 > 4 mg/L: bacteria will not convert Ammonia (NH4) to Nitrate (NO3)
          Ammonia (NH4) Removal
          Good Aerobic Habitat: ORP +100 mV
          NH4 < 0.5 mg/L
MLE with too much Internal Recycle

## Slide 35
Internal Recycle
Secondary
Clarifier
Return Sludge
Aerobic Zone
Anoxic Zone
NH4
N2
NO3
NO3
          Nitrate (NO3) Removal
          Poor Anoxic Habitat: ORP 0 mV or higher
          NO3 > 4 mg/L
          Ammonia (NH4) Removal
          Poor Aerobic Habitat: ORP +50 mV
          NH4 > 0.5 mg/L
MLE with way too much Internal Recycle

## Slide 36
Sequencing Batch Reactor
SBR

## Slide 37
Idle
Air ON
Sequencing Batch Reactor (SBR)
Ammonia (NH4) Removal: Nitrification
Sludge Storage
NO3
NH4
          Ammonia (NH4) Removal
          Target: NH4 < 0.5 mg/L
SBR #1
SBR #2

## Slide 38
Idle
Air OFF
Sequencing Batch Reactor (SBR)
Nitrate (NO3) Removal: Denitrification
Sludge Storage
N2
NO3
          Nitrate (NO3) Removal
          Target: NO3 < 4 mg/L
SBR #1
SBR #2

## Slide 39
Air ON
Decant / Waste
Sequencing Batch Reactor (SBR)
Settle, Decant & Waste Sludge
Sludge Storage
SBR Process Control:
Establish cycle times that are long enough to provide optimal habitats.
And, short enough to allow all of the flow to be nitrified and denitrified.
SBR #1
SBR #2

## Slide 40
Optimizing SBR cycle time
  Too short
          Will not reach +100 mV for Ammonia (NH4) Removal.
          Will not reach -100 mV for Nitrate (NO3) Removal.
          Note: Temperature and BOD affect Air OFF cycle.
  Too long
          Wastewater will pass through tank before all Ammonia (NH4) converted to Nitrate (NO3).
          And, before all Nitrate (NO3) is converted to Nitrogen Gas (N2).
  Just right
          Good habitats …
          ORP of +100 mV for 60 minutes
          And, ORP of -100 mV for 30 minutes.
          Bonus: Changing conditions will serve as a selector.

## Slide 41
Oxidation Ditch

## Slide 42
Secondary
Clarifier
Oxidation Ditch
Anoxic Zone
Aerobic Zone
Anoxic Zone
Aerobic Zone
NH4

## Slide 43
Secondary
Clarifier
Oxidation Ditch
Anoxic Zone
Aerobic Zone
Anoxic Zone
Aerobic Zone
NO3
NH4

## Slide 44
Secondary
Clarifier
Oxidation Ditch
Anoxic Zone
Aerobic Zone
Anoxic Zone
Aerobic Zone
NO3
N2

## Slide 45
Secondary
Clarifier
Oxidation Ditch
Anoxic Zone
Aerobic Zone
Anoxic Zone
Aerobic Zone
NH4

## Slide 46
Secondary
Clarifier
Oxidation Ditch
Anoxic Zone
Aerobic Zone
Anoxic Zone
Aerobic Zone
NO3
NH4

## Slide 47
Secondary
Clarifier
Oxidation Ditch
Anoxic Zone
Aerobic Zone
Anoxic Zone
Aerobic Zone
NO3

## Slide 48
Secondary
Clarifier
Oxidation Ditch
Anoxic Zone
Aerobic Zone
Anoxic Zone
Aerobic Zone
NO3
N2

## Slide 49
Secondary
Clarifier
Oxidation Ditch
Anoxic Zone
Aerobic Zone
Anoxic Zone
Aerobic Zone
          Ammonia (NH4) Removal
          Target: NH4 < 0.5 mg/L
          Nitrate (NO3) Removal
          Target: NO3 of 1-4 mg/L

## Slide 51
Experiment with YOUR plant:
Find the “Right” Process Control Strategy …
SBR
MLE
Oxidation ditch …
          and,
          Optimize Nitrogen Removal!

## Slide 52
Change day-to-day operations to
create ideal habitats for bacteria to remove Nitrogen

## Slide 53
Biological Nitrogen Removal:
Convert LIQUID to GAS …
BOD and TSS Removal:
Convert LIQUID to SOLID …

## Slide 54
Nitrogen Removal
 | 1. Nitrification | 2. Denitrification
 | Ammonia Removal | Nitrate Removal
 | NH4→NO3 | NO3→N2
DO: Dissolved Oxygen | >1 mg/L | <0.3 mg/L
ORP: Oxygen Reduction Potential | >+100 mV | <-100 mV
MLSS | >2500 mg/L | >2500 mg/L
HRT (Hydraulic Retention Time) | >6 hr | ~1 hr
BOD: Biochemical Oxygen Demand | <20 mg/L | >100 mg/L
Alkalinity | >60 mg/L | NA
 | Alkalinity is lost | Alkalinity is gained
Notes: |  | 
> means "greater than" |  | 
< means "less than" |  | 
~ means "approximately“ All numbers are “rules of thumb” |  | 

## Slide 56
Optimize Ammonia (NH4) Removal

## Slide 57
Secondary Clarifier
Aeration Tank
Primary Clarifier
Conventional Activated Sludge Plant
          Ammonia (NH4) Removal
          Target: less than 0.5 mg/L
          Raise mixed liquor
            … the higher the better for N-Removal.
          Keep ORP at +100 mV (or higher) by adjusting DO settings until …
            … enough DO & ORP to reduce NH4 to 0.5 mg/L …
            … but not so much as to move too much DO into Anoxic or waste electricity.
            Warning: pH and Nitrite (NO2)
NH4
NO3

## Slide 58
Step 2:
Optimize Nitrate (NO3) Removal

## Slide 59
Operate Aeration Tank as SBR

## Slide 60
Secondary Clarifier
Aeration Tank
Primary Clarifier
Conventional Activated Sludge operated as SBR
NO3
NH4
          Maintain Ammonia (NH4) Removal
          Target: NH4 < 0.5 mg/L
          ORP: +100 mV long enough
          (60 minutes)

## Slide 61
Secondary Clarifier
Aeration Tank
Primary Clarifier
          Cycle air ON to remove NH4 & OFF to remove NO3
          Use ORP to adjust AirON/AirOFF times
Conventional Activated Sludge operated as SBR
NO3
NH4
NO3
N2
          Maintain Ammonia (NH4) Removal
          Target: NH4 < 0.5 mg/L
          ORP: +100 mV long enough
          (60 minutes)
          Nitrate (NO3) Removal
          Target: NO3 < 4 mg/L
          ORP: -100 mV long enough (30 minutes)
          If habitats are good and NO3 remains high, likely not enough BOD.
          Search for additional BOD.

## Slide 62
Operate Aeration Tank as MLE

## Slide 63
Primary Clarifier
MLE Process Modification of Conventional Activated Sludge Plant
Aeration Tank
Secondary Clarifier
Sludge Holding Tank
NH4
NO3
NO3
N2
          Maintain Ammonia (NH4) Removal
          Target: NH4 < 0.5 mg/L
          ORP: +100 mV
          Nitrate (NO3) Removal
          Target: NO3 < 4 mg/L
          ORP: -100 mV
          Unless RAS can be increased to 200% or more, NO3 target of 4 mg/L will be hard to achieve

## Slide 64
Primary Clarifier
Anoxic Tank
Aeration Tank
Secondary Clarifier
Sludge Holding Tank
NH4
NO3
NO3
N2
          Maybe use Primary Clarifier as pre-Anoxic Tank
          Maybe install Internal Recycle Pump(s)
MLE Process Modification of Conventional Activated Sludge Plant

## Slide 65
Primary Clarifier
Aeration Tank
Secondary Clarifier
Sludge Holding Tank
Anoxic Tank
NH4
NO3
N2
NO3
          Maybe use Sludge Holding Tank or Gravity Thickener as post-Anoxic Tank
MLE Process Modification of Conventional Activated Sludge Plant

## Slide 66
Primary Clarifier
Aeration Tank
Secondary Clarifier
Sludge Holding Tank
Anoxic Tank
NH4
NO3
N2
NO3
          Or, modify operations to incorporate SBR and MLE Processes
NO3
N2
MLE Process Modification of Conventional Activated Sludge Plant

## Slide 68
Chinook, Montana Population: 1,250 0.5 MGD design flow

## Slide 70
Conrad, Montana Population: 2,500 0.5 MGD design flow

## Slide 72
Upton, Massachusetts Population: 5,600 0.5 MGD design flow

## Slide 74
Cookeville, Tennessee Population: 33,500 15 MGD design flow

## Slide 76
Palmer, Massachusetts Population: 12,200 5.6 MGD design

## Slide 78
Helena, Montana Population: 31,500 5.4 MGD design flow

## Slide 80: Comments & Questions
Grant Weaver
g.weaver@cleanwaterops.com