## Slide 1
Phosphorus Removal
University of Kansas
100th Annual Water and Wastewater School
Lawrence, Kansas
July 30, 2019
Grant Weaver, PE & wastewater operator
G.Weaver@CleanWaterOps.com

## Slide 2: Operational Strategies for Nutrient Removal
Nutrient Removal Overview
Nitrogen Removal
Science & Technology
Applying what we’ve learned
Phosphorus Removal
Science & Technology
Applying what we’ve learned
Aero-Mod Phosphorus and Nitrogen Removal

## Slide 4
Wastewater Science
Alkalinity and pH

## Slide 5
Wastewater Science
DO and ORP
DO (Dissolved Oxygen)
ORP (Oxygen Reduction Potential)

## Slide 8
Phosphorus Removal:
What an Operator needs to know
  ONE. Convert soluble phosphorus to TSS …
  Biologically
  Chemically
  TWO. Remove TSS

## Slide 9
Biological Phosphorus Removal
  Step 1: prepare “dinner”
  VFA (volatile fatty acids) production in anaerobic/fermentive conditions
  Step 2: “eat”
  Bio-P bugs (PAOs) eat VFAs in anaerobic/fermentive conditions … temporarily releasing more P into the water
  Step 3: breathe and grow
  Bio-P bugs (PAOs) take in almost all of the soluble P in aerobic conditions as they grow and reproduce

## Slide 10
Phosphorus Removal:
What an Operator needs to know
  orthophosphate = soluble phosphorus
  ortho-Phosphate, reactive phosphorus, phosphate, ortho-P, PO4, PO4=, PO4-2
  total-Phosphorus = soluble + particulate phosphorus
  phosphorus, total-P, TP, t-P, tP, P

## Slide 11
Typical plant
Influent phosphorus: 6 mg/L
Effluent phosphorus: 3 mg/L
Effluent TSS: 15 mg/L
Effluent total-P = particulate P + soluble P
How much effluent phosphorus is soluble and how much is in the TSS?
Approximately 1% of effluent TSS (conventional plant) is phosphorus …
Effluent P = particulate P + soluble P
Particulate (P in the TSS): 15 mg/L TSS x 0.01 = 0.15 mg/L
Soluble = 3 mg/L – 0.15 mg/L with TSS = 2.85 mg/L

## Slide 12
Chart: Example: effluent phosphorus (mg/L) Before Phosphorus Removal (Biological or Chemical)
| Particulate | Soluble
 | 0.15 | 2.85

## Slide 13
Converting SOLUBLE phosphorus to PARTICULATE phosphorus
Biological Phosphorus removal, when fully optimized, will remove all but 0.05 mg/L of the soluble Phosphorus
and
Chemical Phosphorus removal, the same, all but 0.05 mg/L
Either way, only 0.05 mg/L of soluble Phosphorus remains; most all of it is particulate Phosphorus … that is, effluent TSS
Meanwhile …
The vast majority of the soluble phosphorus is converted to particulate phosphorus; increasing the percentage of the MLSS and TSS that is P from ~1% to ~5%

## Slide 14
Chart: Example: effluent phosphorus (mg/L) After Phosphorus Removal (Biological or Chemical)
| Particulate | Soluble
 | 0.75 | 0.05

## Slide 15
TSS Removal Requirements
Since all but 0.05 mg/L of the soluble Phosphorus can be converted to TSS Phosphorus (Biologically and/or Chemically)
And, because approximately 5% of Effluent TSS is Phosphorus
… To meet a total-P limit, the effluent TSS needs to be kept to the max TSS number shown in the table.
P Limit | max TSS
0.1 | 1
0.2 | 3
0.3 | 5
0.4 | 7
0.5 | 9
0.6 | 11
0.7 | 13
0.8 | 15
0.9 | 17
1.0 | 19
1.1 | 21
1.2 | 23
1.3 | 25
1.4 | 27
1.5 | 29

## Slide 16
Phosphorus Removal without Facility Upgrades
 | total-Phosphorus (mg/L) |  | 
 | before | after | 
Conrad, Montana | 2.1 | 0.15 | 
Keene, New Hampshire | 1.0 | 0.20 | 50% less chemicals
Chinook, Montana | 2.8 | 0.30 | 
East Haddam, Connecticut (2 month trial) | 3.5 | 0.35 | 
Palmer, Massachusetts | 0.5 | 0.50 | 25% less chemicals
Westfield, Massachusetts | 0.5-2.5 | 0.50 | 50% less chemicals
Athens, Tennessee: Oostanaula | 0.5 | 0.50 | 100% less chemicals
Plainfield, Connecticut: Village Plant | 2.5 | 0.70 | 
Suffield, Connecticut | 3.0 | 0.70 | 
Cookeville, Tennessee | 2.0 | 1.4 | 
Helena, Montana | 2.9 | 0.5-2.0 | 
Athens, Tennessee: North Mouse Creek | 2.8 | 0.3-3.0 | 

## Slide 17
Biological Phosphorus Removal:
Mainstream Flow Fermentation Processes

## Slide 18
Primary Clarifier
Bio-P Removal: Mainstream Fermentation Process
Aeration Tank
Secondary Clarifier
Anaerobic Tank
Gravity Thickener
Sludge Storage
In Anaerobic Tank …
Bacteria break down complex BOD into VFAs (volatile fatty acids).
VFAs

## Slide 19
Primary Clarifier
Bio-P Removal: Mainstream Fermentation Process
Aeration Tank
Secondary Clarifier
PO4
Anaerobic Tank
Gravity Thickener
Sludge Storage
In Anaerobic Tank …
Bacteria break down complex BOD into VFAs (volatile fatty acids).
PAO bacteria (phosphate accumulating organisms) take in VFAs as energy source & temporarily release PO4 (phosphate) into solution.
VFAs

## Slide 20
Primary Clarifier
Bio-P Removal: Mainstream Fermentation Process
Aeration Tank
Secondary Clarifier
PO4
Anaerobic Tank
Gravity Thickener
Sludge Storage
In Anaerobic Tank …
Bacteria break down complex BOD into VFAs (volatile fatty acids).
PAO bacteria (phosphate accumulating organisms) take in VFAs as energy source & temporarily release PO4 (phosphate) into solution.
In Aeration Tank …
Energized PAO bacteria take PO4 out of solution.

## Slide 21
Primary Clarifier
Bio-P Removal: Mainstream Fermentation Process
Aeration Tank
Secondary Clarifier
Anaerobic Tank
PO4
Gravity Thickener
Sludge Storage
In Anaerobic Tank …
Bacteria break down complex BOD into VFAs (volatile fatty acids).
PAO bacteria (phosphate accumulating organisms) take in VFAs as energy source & temporarily release PO4 (phosphate) into solution.
In Aeration Tank …
Energized PAO bacteria take PO4 out of solution.

## Slide 22
Primary Clarifier
Bio-P Removal: Mainstream Fermentation Process
Aeration Tank
Secondary Clarifier
Anoxic Tank
Gravity Thickener
Sludge Storage
Pre-anoxic zone to …
Strengthen anaerobic conditions in anaerobic tank
Minimize VFA use by denitrifying bacteria – the ones that convert Nitrate (NO3) to Nitrogen Gas (N2) – by “feeding” influent to the denitrifiers.
PO4
Anaerobic Tank
VFAs

## Slide 23
Primary Clarifier
Bio-P Removal: Mainstream Fermentation Process
Aeration Tank
Secondary Clarifier
Anoxic Tank
Gravity Thickener
Sludge Storage
Pre-anoxic zone to …
Strengthen anaerobic conditions in anaerobic tank
Minimize VFA use by denitrifying bacteria – the ones that convert Nitrate (NO3) to Nitrogen Gas (N2) – by “feeding” influent to the denitrifiers.
PO4
Anaerobic Tank

## Slide 24
Primary Clarifier
Bio-P Removal: Mainstream Fermentation Process
Aeration Tank
Secondary Clarifier
Anoxic Tank
Gravity Thickener
Sludge Storage
Pre-anoxic zone to …
Strengthen anaerobic conditions in anaerobic tank
Minimize VFA use by denitrifying bacteria – the ones that convert Nitrate (NO3) to Nitrogen Gas (N2) – by “feeding” influent to the denitrifiers.
PO4
Anaerobic Tank

## Slide 25
Biological Phosphorus Removal: Combined Sidestream & Mainstream Fermentation

## Slide 26
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Aeration Tank
Secondary Clarifier
Anaerobic Tank
Gravity Thickener
Sludge Storage
VFAs
Fermentation

## Slide 27
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Aeration Tank
Secondary Clarifier
Anaerobic Tank
Gravity Thickener
Sludge Storage
VFAs
Fermentation

## Slide 28
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Aeration Tank
Secondary Clarifier
VFAs
Anaerobic Tank
Gravity Thickener
Sludge Storage
Fermentation

## Slide 29
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Aeration Tank
Secondary Clarifier
PO4
Anaerobic Tank
Gravity Thickener
Sludge Storage
Fermentation

## Slide 30
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Aeration Tank
Secondary Clarifier
Anaerobic Tank
PO4
          Nitrogen Interference:
          Nitrate (NO3) will consume VFAs
Gravity Thickener
Sludge Storage
Fermentation

## Slide 31
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Secondary Clarifier
Gravity Thickener
Sludge Storage
Fermentation
          No Nitrogen Interference!
Anoxic Tank
Anaerobic Tank
Aeration Tank

## Slide 32
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Secondary Clarifier
Gravity Thickener
Sludge Storage
Fermentation
          No Nitrogen Interference!
Anoxic Tank
Anaerobic Tank
Aeration Tank
VFAs

## Slide 33
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Secondary Clarifier
Gravity Thickener
Sludge Storage
Fermentation
          No Nitrogen Interference!
Anoxic Tank
Anaerobic Tank
Aeration Tank
PO4

## Slide 34
Primary Clarifier
Bio-P Removal: Sidestream Fermentation Process
Secondary Clarifier
Gravity Thickener
Sludge Storage
Fermentation
          No Nitrogen Interference!
Anoxic Tank
Anaerobic Tank
Aeration Tank
PO4

## Slide 35
Optimizing Bio-P Removal:
Mainstream or Sidestream Fermentation
  Anaerobic Tank
          2 hour HRT*
          ORP of -200 mV*
          25 times as much BOD as influent ortho-P*
          Ortho-P release (3 times influent ortho-P)*
  Aeration Tank
          DO of 2.0 mg/L
          ORP of +150 mV
          pH of 7.0+*
          Ortho-P concentration of 0.05 mg/L*
          *Approximate: Every Plant is Different

## Slide 37
Review: Biological Phosphorus Removal
  Step 1: prepare “dinner”
  VFA (volatile fatty acids) production in anaerobic/fermentive conditions
  Step 2: “eat”
  Bio-P bugs (PAOs) eat VFAs in anaerobic/fermentive conditions … temporarily releasing more P into the water
  Step 3: breathe and grow
  Bio-P bugs (PAOs) take in almost all of the soluble P in aerobic conditions as they grow and reproduce

## Slide 38
Optimizing Bio-P Removal:
Mainstream or Sidestream Fermentation
  Anaerobic Tank
          2 hour HRT*
          ORP of -200 mV*
          25 times as much BOD as influent ortho-P*
          Ortho-P release (3 times influent ortho-P)*
  Aeration Tank
          DO of 2.0 mg/L
          ORP of +150 mV
          pH of 7.0+*
          Ortho-P concentration of 0.05 mg/L*
          *Approximate: Every Plant is Different

## Slide 39
Experiment with YOUR plant:
Find the “Right” Process Control Strategy …
Sidestream
Mainstream
Both …
          and,
          Optimize Phosphorus Removal!

## Slide 40
Create a Sidestream Fermentation Zone

## Slide 41
Primary Clarifier
Bio-P Removal: Grant’s Sidestream Process
Aeration Tank
Secondary Clarifier
Gravity Thickener
Sludge Storage
Fermenter

## Slide 42
Primary Clarifier
Bio-P Removal: Grant’s Sidestream Process
Secondary Clarifier
Gravity Thickener
Fermenter
VFAs
PO4
Aeration Tank

## Slide 43
Primary Clarifier
Bio-P Removal: Grant’s Sidestream Process
Secondary Clarifier
Gravity Thickener
Fermenter
PO4
Aeration Tank

## Slide 44
Primary Clarifier
Bio-P Removal: Grant’s Sidestream Process
Secondary Clarifier
Gravity Thickener
Fermenter
PO4
Aeration Tank

## Slide 45
Primary Clarifier
Bio-P Removal: Grant’s Sidestream Process
Secondary Clarifier
PO4
Gravity Thickener
Fermenter
Aeration Tank

## Slide 46
Optimizing Bio-P Removal: Mainstream, Sidestream or Combination Fermentation
  Anaerobic Tank
          2 hour HRT*
          ORP of -200 mV*
          25 times as much BOD as influent ortho-P*
          Ortho-P release (3 times influent total-P)*
  Aeration Tank
          High DO (2.0 mg/L*)
          High ORP (+150 mV*)
          pH of 6.8+*
          Ortho-P concentration of 0.05 mg/L*
          *Approximate: Every Plant is Different

## Slide 47
Create a Mainstream Fermentation Zone

## Slide 48
Mainstream Bio-P Removal in Conventional Activated Sludge Plant
Anaerobic Tank
Primary Clarifier
Aeration Tank
Secondary Clarifier
Sludge Storage
Gravity Thickener
VFAs

## Slide 49
Anaerobic Tank
Primary Clarifier
Aeration Tank
Secondary Clarifier
PO4
Sludge Storage
Gravity Thickener
VFAs
Mainstream Bio-P Removal in Conventional Activated Sludge Plant

## Slide 50
Anaerobic Tank
Primary Clarifier
Aeration Tank
Secondary Clarifier
PO4
Sludge Storage
Gravity Thickener
Mainstream Bio-P Removal in Conventional Activated Sludge Plant

## Slide 51
Anaerobic Tank
Primary Clarifier
Aeration Tank
Secondary Clarifier
PO4
Sludge Storage
Gravity Thickener
Mainstream Bio-P Removal in Conventional Activated Sludge Plant

## Slide 54
Change day-to-day operations to
create ideal habitats for bacteria to remove Phosphorus

## Slide 55
Conrad, Montana Population: 2,500 0.5 MGD design flow

## Slide 57
Chinook, Montana Population: 1,250 0.5 MGD design flow

## Slide 59
Palmer, Massachusetts Population: 12,200 5.6 MGD design

## Slide 61: Comments & Questions
Grant Weaver
g.weaver@cleanwaterops.com